## TAS IO Database
Units | Tag Number | Instrument Name | Description | Location | Quantity | I/O Type | Signal Type | Zero | Span | Unit
Entrance Gate | ZS-I1 | Electric Actuator | Truck Arrival Detection | I1 | 1 | DI | 24V DC | 0 | 1 | -
Exit Gate | ZS-O1 | Electric Actuator | Truck Departure Detection | O1 | 1 | DI | 24V DC | 0 | 1 | -
Inbound Weighing Unit | BS-S2 | Barcode Scanner | Inbound SO/Vehicle ID | S2 | 1 | Data | Ethernet/TCP | - | - | -
Diesel Bay Unit | BS-S3a01 | Barcode Scanner | Inbound SO/Vehicle ID | S3a-01 | 1 | Data | Ethernet/TCP | - | - | -
Diesel Bay Unit | BS-S3a02 | Barcode Scanner | Inbound SO/Vehicle ID | S3a-02 | 1 | Data | Ethernet/TCP | - | - | -
Diesel Bay Unit | BS-S3a03 | Barcode Scanner | Inbound SO/Vehicle ID | S3a-03 | 1 | Data | Ethernet/TCP | - | - | -
Diesel Bay Unit | BS-S3a04 | Barcode Scanner | Inbound SO/Vehicle ID | S3a-04 | 1 | Data | Ethernet/TCP | - | - | -
Gasohol95 Bay Unit | BS-S3b01 | Barcode Scanner | Inbound SO/Vehicle ID | S3b-01 | 1 | Data | Ethernet/TCP | - | - | -
Gasohol95 Bay Unit | BS-S3b02 | Barcode Scanner | Inbound SO/Vehicle ID | S3b-02 | 1 | Data | Ethernet/TCP | - | - | -
Outbound Weighing Unit | BS-S4 | Barcode Scanner | Inbound SO/Vehicle ID | S4 | 1 | Data | Ethernet/TCP | - | - | -
Inbound Weighing Unit | WT-S2 | Inbound Load Sensors | Tare Weight Acquisition | S2 | 4 | AI | 0 - 20 mA | 0 | 30000 | kg
Outbound Weighing Unit | WT-S4 | Outbound Load Sensors | Gross Weight Acquisition | S4 | 4 | AI | 0 - 20 mA | 0 | 30000 | kg
Diesel Storage Unit | LIT-S3101 | Diesel Tank Level Transmitter | Inventory Management | S3 | 1 | AI | 0 - 20 mA | 0 | 5 | m
Diesel Storage Unit | PIT-S3101 | Diesel Tank Pressure Transmitter | Safety Monitoring | S3 | 1 | AI | 0 - 20 mA | 0 | 10 | bar
Diesel Storage Unit | TIT-S3101 | Diesel Tank Temperature Transmitter | Density Compensation | S3 | 1 | AI | 0 - 20 mA | 0 | 100 | °C
Gasohol95 Storage Unit | LIT-S3102 | Gasohol Tank Level Transmitter | Inventory Management | S3 | 1 | AI | 0 - 20 mA | 0 | 5 | m
Gasohol95 Storage Unit | PIT-S3102 | Gasohol Tank Pressure Transmitter | Safety Monitoring | S3 | 1 | AI | 0 - 20 mA | 0 | 10 | bar
Gasohol95 Storage Unit | TIT-S3102 | Gasohol Tank Temperature Transmitter | Density Compensation | S3 | 1 | AI | 0 - 20 mA | 0 | 100 | °C
Diesel Bay Unit | FT-S3a01 | Flowmeter | Filling Measurement | S3a-01 | 1 | AI | 0 - 20 mA | 0 | 1000 | L/min
Diesel Bay Unit | XV-S3a01 | Solenoid Valve | Flow Cut-off | S3a-01 | 1 | DO | 24V DC | 0 | 1 | -
Diesel Bay Unit | P-S3a01 | Centrifugal Pump | Product Transfer | S3a-01 | 1 | DO | 24V DC | 0 | 1 | -
Diesel Bay Safety Unit | VT-S3a01 | Vibration Sensor | Safety Interlock | S3a-01 | 1 | AI | 0 - 20 mA | 0 | 25 | mm/s
Diesel Bay Safety Unit | GS-S3a01 | Truck Grounding | Safety Interlock | S3a-01 | 1 | DI | 24V DC | 0 | 1 | -
Diesel Bay Unit | FT-S3a02 | Flowmeter | Filling Measurement | S3a-02 | 1 | AI | 0 - 20 mA | 0 | 1000 | L/min
Diesel Bay Unit | XV-S3a02 | Solenoid Valve | Flow Cut-off | S3a-02 | 1 | DO | 24V DC | 0 | 1 | -
Diesel Bay Unit | P-S3a02 | Centrifugal Pump | Product Transfer | S3a-02 | 1 | DO | 24V DC | 0 | 1 | -
Diesel Bay Safety Unit | VT-S3a02 | Vibration Sensor | Safety Interlock | S3a-02 | 1 | AI | 0 - 20 mA | 0 | 25 | mm/s
Diesel Bay Safety Unit | GS-S3a02 | Truck Grounding | Safety Interlock | S3a-02 | 1 | DI | 24V DC | 0 | 1 | -
Diesel Bay Unit | FT-S3a03 | Flowmeter | Filling Measurement | S3a-03 | 1 | AI | 0 - 20 mA | 0 | 1000 | L/min
Diesel Bay Unit | XV-S3a03 | Solenoid Valve | Flow Cut-off | S3a-03 | 1 | DO | 24V DC | 0 | 1 | -
Diesel Bay Unit | P-S3a03 | Centrifugal Pump | Product Transfer | S3a-03 | 1 | DO | 24V DC | 0 | 1 | -
Diesel Bay Safety Unit | VT-S3a03 | Vibration Sensor | Safety Interlock | S3a-03 | 1 | AI | 0 - 20 mA | 0 | 25 | mm/s
Diesel Bay Safety Unit | GS-S3a03 | Truck Grounding | Safety Interlock | S3a-03 | 1 | DI | 24V DC | 0 | 1 | -
Diesel Bay Unit | FT-S3a04 | Flowmeter | Filling Measurement | S3a-04 | 1 | AI | 0 - 20 mA | 0 | 1000 | L/min
Diesel Bay Unit | XV-S3a04 | Solenoid Valve | Flow Cut-off | S3a-04 | 1 | DO | 24V DC | 0 | 1 | -
Diesel Bay Unit | P-S3a04 | Centrifugal Pump | Product Transfer | S3a-04 | 1 | DO | 24V DC | 0 | 1 | -
Diesel Bay Safety Unit | VT-S3a04 | Vibration Sensor | Safety Interlock | S3a-04 | 1 | AI | 0 - 20 mA | 0 | 25 | mm/s
Diesel Bay Safety Unit | GS-S3a04 | Truck Grounding | Safety Interlock | S3a-04 | 1 | DI | 24V DC | 0 | 1 | -
Gasohol95 Bay Unit | FT-S3b01 | Flowmeter | Filling Measurement | S3b-01 | 1 | AI | 0 - 20 mA | 0 | 1000 | L/min
Gasohol95 Bay Unit | XV-S3b01 | Solenoid Valve | Flow Cut-off | S3b-01 | 1 | DO | 24V DC | 0 | 1 | -
Gasohol95 Bay Unit | P-S3b01 | Centrifugal Pump | Product Transfer | S3b-01 | 1 | DO | 24V DC | 0 | 1 | -
Gasohol95 Bay Safety Unit | VT-S3b01 | Vibration Sensor | Safety Interlock | S3b-01 | 1 | AI | 0 - 20 mA | 0 | 25 | mm/s
Gasohol95 Bay Safety Unit | GS-S3b01 | Truck Grounding | Safety Interlock | S3b-01 | 1 | DI | 24V DC | 0 | 1 | -
Gasohol95 Bay Unit | FT-S3b02 | Flowmeter | Filling Measurement | S3b-02 | 1 | AI | 0 - 20 mA | 0 | 1000 | L/min
Gasohol95 Bay Unit | XV-S3b02 | Solenoid Valve | Flow Cut-off | S3b-02 | 1 | DO | 24V DC | 0 | 1 | -
Gasohol95 Bay Unit | P-S3b02 | Centrifugal Pump | Product Transfer | S3b-02 | 1 | DO | 24V DC | 0 | 1 | -
Gasohol95 Bay Safety Unit | VT-S3b02 | Vibration Sensor | Safety Interlock | S3b-02 | 1 | AI | 0 - 20 mA | 0 | 25 | mm/s
Gasohol95 Bay Safety Unit | GS-S3b02 | Truck Grounding | Safety Interlock | S3b-02 | 1 | DI | 24V DC | 0 | 1 | -